SURGE ELIMINATION & POWER CONDITIONER (SX-1216-RTi)

1) 용  도

본 기기는 기기의 오작동 및 다운타임을 유발할 수 있는 과도한 전류로부터 AV 장비를 보호하기 위한 파워 컨디셔너로써 전원의 원격 조정이 가능하다. 스위치형 콘센트는 5~30VDC 전압과 함께 컨트롤이 가능하며 후면 패널의 Phonix 커넥터에 연결된 폐쇄 스위치와 접촉한다. 또한 커넥터는 여러 장치를 캐스캐이드 하여 사용할 수 있고, 중앙 제어 장치로 사용할 수 있다. 연결된 장비가 서지, 스파이크, 과도 전류 및 노이즈로부터 보호되도록 모든 서지 에너지를 제거한다. AV장비의 성능을 저하시키는 혼합접지나 커먼모드 잡음과 같은 부작용을 일으키지 않으면서 최대 6,000V까지 전압이 급등하는 것을 차단한다. 또한 완전한 전원 컨디션 솔루션을 위한 커먼모드와 노멀모드 Impedance TolerantⓇ EMI/RFI filtering; SurgeX ICEⓇ -Inrush Current Elimination and COUVSⓇ -Catastrophic Over/Under Voltage Shutdown 기능을 가지고 있다. 노멀모드, 커먼 모드 노이즈를 제거하고, 실제 소스 및 로드 임피던스를 더욱 수용하도록 설계되어 깨끗하고 일관된 전원을 공급받을 수 있도록 한다.

2) 기  능

- 자기 차폐 금속 케이스

- 후면 패널의 10채널 AC콘센트 (8개 스위치, 2개 상시전원)

- 전면 패널의 1채널 AC콘센트

- EMI / RFI 필터

- COUVS® 과전압 또는 과소 전압 폐쇄

- SurgeX ICE® 전압 유입 제거

- 과부화 방지 차단기

- 최대 6,000V의 서지 에너지 제거

3) 사  양

- Power Configuration : 16 amps @ 230 volts, 50Hz / 60Hz

- Power Requirement (no load): 6 watts.

- Surge Let-Through Voltage (6000-volt surge): 0 volts.

- Safety Certification : IEC/EN 61643-1

- Performance Rating: Grade A, Class 1, Mode 1

- Maximum Applied Surge Voltage: 6000 volts

- Undervoltage Shutdown : 180 volts (auto resetting)

- Overvoltage Shutdown : 280 volts (auto resetting)

- Maximum Load Inrush Current During Power-up : 1000 Joules

- Remote Turn-on Applied Voltage Range: 5 to 30 volts DC

- Auxiliary Relay Contact Rating: 30 Volts at 1 Amp

- Dimensions (WxHxD): 483 x 45 x 267 mm

- Weight: 5 kg